## Slide 1: Optimisation of Design & Operation of Generators for Offshore VAWTs
Author: Michael Argent
Email: michael.argent@strath.ac.uk
Supervisors: Alasdair McDonald, Bill Leithead

## Slide 2: Overview
Background
Generator Modelling
Torque Harmonics
Generator Losses
Optimisation
Future Work
Questions

## Slide 3: Research Background
Increasing interest in offshore VAWTs
PhD focus on VAWT powertrains:
  Will cost more than HAWT equivalents
  Need to evaluate CoE impact of powertrain as part of assessing viability of VAWTs
Attractions | Challenges
Lower powertrain mounting* | Increased torque (slower speed)
No cyclic self-weight effects | Cyclic torque => fatigue
No yaw/pitch* mechanisms | Lower aerodynamic efficiency
*Applies to some VAWT designs only | 

## Slide 4: VAWT Powertrain Options
Many top-level design decisions on VAWT
Research to optimise powertrain selection for given VAWT design (size, rotor design, etc…)
Currently focusing on generator costs/losses/output
Criteria | Potential Design Options |  | baseline spec
Turbine Power/Size | 5MW | 10MW | 20MW
Rotor Design | H-rotor | V-rotor | Darrieus
No of Blades | Two | Three | …
Swept Area Aspect | Narrow | Medium | Wide
Gearing | Direct Drive | Single Stage | Multiple Stage
Generator Type | PMG | DFIG | …
No of Generators | One | Multiple | …

## Slide 5: Torque Harmonics & Control
Cyclic TMECH => Fourier Series
  Mean & series of torque harmonics
  Losses calculated separately
Generator behaviour: T imbalance
Controlling TELEC affects response
  (q=0 Fixed Torque, q=1 Fixed Speed)
Rotor speed is affected accordingly by q
q is applied to each torque harmonic proportionally

## Slide 6
Generator (Stator & Rotor)
Represented by
Generator Segment (Pole Pair)
Electric Circuit
Magnetic Circuit
Modelled
Airgap Flux Density & Stator (iron losses)
Electric Torque prop to Current Stator Current (copper losses)
Generator Model Overview (DDPMG)

## Slide 7: Generator Losses
Copper Losses | Iron Losses
Varying TELEC (q>0) => varying current I | Varying rotor speed (q<1) => varying fELEC
Integrate I2R losses => mean power loss | Swing eq. into , integrate
loss ∝ q2 | loss ∝ (1-q)
Large magnitude harmonics dominate | Lower order harmonics more important
Copper Losses | Iron Losses
Varying TELEC (q>0) => varying current I | Varying rotor speed (q<1) => varying fELEC
Integrate I2R losses => mean power loss | 
loss ∝ q2 | loss ∝ (1-q)
Large magnitude harmonics dominate | Lower order harmonics more important
Cu losses dominate
Fe losses dominate
Losses Minimised

## Slide 8: Losses at different wind speeds
Minimise Fe Losses
Minimise Cu Losses
Annual Energy Losses |  | 
Torque Factor q | Losses [MWh] | % Loss (vs q=0)
0 | 504.3 | 0.0%
0.2 | 503.7 | -0.1%
0.4 | 513.4 | +1.8%
0.6 | 533.3 | +5.8%
0.8 | 563.6 | +11.8%
1 | 604.1 | +19.8%
qOPT | 499.7 | -0.9%
Energy Loss Contribution from mean & 2nd harmonic
99.63%
99.70%
99.76%
99.80%
99.84%
99.86%

## Slide 9: Peak Torque Loading
Max q allowed at rated speed (qMAX) determines TRATED
Running qOPT loss-minimisation strategy reduces TPEAK experienced
Opportunity to reduce TRATED & thus the generator cost

## Slide 10: Mechanical Power Loss
Does varying rotor speed (q<1) affect energy extraction?
Mechanical power loss from deficiency in torque produced by rotor.
For most q mean power output is comparable
Noticeable drop in mean power output when q > 0.8
  Mechanical torque goes negative at points during each revolution
  Likely to avoid running in this area

## Slide 11: Generator Optimisation Algorithm
Two optimisation loops in Algorithm
  Outer loop: Generator Design
  Inner loop: Control Strategy
Aerodynamic torque calculated (all v, q) before main algorithm (TMECH read in)
    Control loop determines optimal q for each wind speed (max power out).
    Annual Yield sums up POPT (Weibull)
    Design optimisation objective function:
Baseline Generator
VAWT Rotor Design
Site Wind
Parameters
Powertrain
Design Type
Unit Costs
& Prices
Aerodynamic
Torque
Dependant Variables
Optimise Control Strategy
qOPT(v)
Eqv. Magnetic Circuit
Eqv. Electric Circuit
Cyclic Torque
Annual Yield
Optimise Generator Design
“profit”
Optimised Generator
TMECH(v,q)
P(v,q)
qOPT(v), POPT(v)
q
v
(wind
Speed)
generator
parameters

## Slide 12: Generator Optimisation Results
Generator Specification | Default | Optimised | Bounds / Diff
Stack Length (m) | 2.5 | 1.68 | [0.5,8.0]
Stator Radius (m) | 5.5 | 8.0 | [2.0,8.0]
No. of Pole Pairs | 160 | 150 | [50,480]
 | 80% | 60% | [60%,100%]
Magnet Height (mm) | 30 | 48 | [15,50]
Energy Yield (GWh) | 48.41 | 49.44 | +2.1%
Copper Loss (GWh) | 1.63 | 0.82 | -50%
Iron Loss (GWh) | 0.66 | 0.45 | -32%
Generator Active Cost (M€) | 0.932 | 1.015 | +8.9%
10 year “Profit” (M€) | 91.04 | 92.91 | +2.1%
Generator Specification | Default | Optimised | Bounds / Diff
Stack Length (m) | 2.5 | 1.68 | [0.5,8.0]
Stator Radius (m) | 5.5 | 8.0 | [2.0,8.0]
No. of Pole Pairs | 160 | 150 | [50,480]
 | 80% | 60% | [60%,100%]
Magnet Height (mm) | 30 | 48 | [15,50]
Energy Yield (GWh) | 48.41 | 49.44 | +2.1%
Copper Loss (GWh) | 1.63 | 0.82 | -50%
Iron Loss (GWh) | 0.66 | 0.45 | -32%
Generator Active Cost (M€) | 0.932 | 1.015 | +8.9%
10 year “Profit” (M€) | 91.04 | 92.91 | +2.1%

## Slide 13: Generator Optimisation Results
Profit +2.1% (energy yield)

## Slide 14: Future Work
Alternative turbine designs (V-rotor, variable pitch, 3 bladed, rescaling [moment of inertia])
Modelling other powertrain components
Cost of Energy contribution of failure of powertrain components

## Slide 15: Conclusion
Evaluation of viability requires complete cost & benefit analysis
To allow for fair comparison both design and operation have to be optimised
This research parametrised torque control and showed its knock-on effects on losses and costs
Conducting optimisation at highest level possible allows for better evaluation of VAWT viability.
Notes: Adjusting the torque control strategy of a VAWT generator can lead to potential loss reductions
  Running a variable q strategy for different wind speeds can lead to the biggest loss reductions.
    Fixed speed strategy at low wind speeds
    Reducing electrical torque variation at high wind speeds
The total losses can be approximated using a sinusoidal torque variation.
  Still need to consider all harmonics for peak torque
Loss minimisation strategy reduces the peak torque and offers the opportunity to specify a generator with a lower torque rating.

## Slide 16
Questions ?
futurewind 2017 is sponsored by:
Organised by the Wind & Marine Energy Systems CDT