## Slide 1: Review of Offshore Cable Reliability Metrics
John Warnock
john.warnock@strath.ac.uk
David McMillan

## Slide 2: Why Review the Metrics
Lack of transparency when it comes to offshore cable reliability
No clear database collating the information that is publically available
To compare the failure rates being estimated to those being experienced
To analyse the impact of a failure

## Slide 3: Literature
Technology | Cable Rating | Failure rate (failures/year) | Year | Reference
HVDC | 320 kV | Best: 0.00001107 | 2015 | A Reliability Evaluation of Offshore HVDC Grid Configuration Options [1]
 |  | Middle: 0.00002213 |  | 
 |  | Worst: 0.0003689 |  | 
HVAC | 60 – 500 kV | 0.000000101 | 2012 | Calculating Target Availability Figures for HVDC Interconnectors [2] / Update of service experience of HV underground and submarine cables [3] / Third-Party Damage to Underground and Submarine Cables [4]
HVDC | 60 – 500 kV | 0.000000163 |  | 
EHVAC | 700 – 800 kV | Single Circuit: 0.3 | 2010 | Reliability study methodology for HVDC grids [5]
 |  | Double Circuit: 0.03 |  | 
HVDC | 600 – 650 kV | Single Pole: 0.4 |  | 
 |  | Double Pole: 0.03 |  | 
HVAC | 132 kV 3 Core | 0.25 | 2007 | Subsea connections to high capacity offshore windfarms [6]
 | 220 kV 3 Core | 0.46 |  | 
 | 400 kV 3 Core | 0.67 |  | 
 | 275 kV Single Core | 0.15 |  | 
 | 400 kV Single Core | 0.22 |  | 
MVAC | 30 kV | Feeder Cable: 0.003 | 2006 | Reliability of Collection Grids for Large offshore Wind Parks [7]
 |  | Tower – Tower Cable: 0.0125 |  | 
 |  | Tower Cable: 0.1875 |  | 
M/HVAC | 33 – 150 kV | Submarine: 0.00000467 | 2006 | Probabilistic Reliability Calculations for the Grid Connection of and Offshore Wind Farm [8]
 |  | Inter-Array: 0.0000323 |  | 
Notes: Concerned that this may be hard to read

## Slide 4: Publically Available Information
Technology | Cable Rating | Failure rate (failures/year) | Year | Reference
MVAC | 11 kV | 0.0625 | 2000 – 2016 | Blyth [9]
MVAC | 33 kV | 0.167 | 2004 – 2016 | Scroby Sands [10,11]
HVAC | 132 kV | 0.5 | 2010 – 2016 | Thanet [12,13,14]
HVAC | 132 kV | 0.25 | 2012 – 2016 | Walney [15]
HVAC | 132 kV | 0.167 | 2010 - 2016 | Robin Rigg [16]
HVAC | 150 kV | 0.0714 | 2002 – 2016 | Horns Rev [17]
HVAC | 150 – 170 kV | 0.5 | 2012 – 2016 | London Array [18]
HVAC | 220 – 245 kV | 1 | 2013 – 2016 | Anholt [19]
HVAC | 132 kV | 1 | 2015 – 2016 | Walney 2 [20]
HVAC | 132 kV | 3 | 2015 – 2016 | Gwynt Y Mor [21,22]

## Slide 5: Comparison of Results

## Slide 6: Comparison of Results

## Slide 7: Early Life Failures

## Slide 8: Causes of Failures
Fishing – anchors / trawling?
Manufacturing faults becoming apparent when cables are energised
Jack up vessels during installation
Cable movement
Cable protection
  Exposed cable

## Slide 9: CIGRE Results
Figures much smaller than those observed for wind farms
Most likely due to
  7,000 km of cable
  Different conditions
  Large range of capacities

## Slide 10: Conclusions
The figures found in the literature agree with those witnessed in offshore wind farms
High early life failure rates
Not enough data available – withheld by insurance companies etc.
CIGRE data should not be used in calculations
Greater need for transparency in the field

## Slide 11: References
[1] C. MacIver, K. R. W. Bell and D. P. Nedic, “A Reliability Evaluation of Offshore HVDC Grid Configuration Options.” University of Strathclyde, (2013).
[2] Sinclair Knight Merz. "Calculating Target Availability Figures for HVDC Interconnectors", ofgem, (2012).
[3] CIGRE working group B1.10. “Update of service experience of HV underground and submarine cables”, (2009).
[4] CIGRE working group B1.21. “Third-Party Damage to Underground and Submarine Cables”, (2009).
[5] K. Linden, B. Jacobson, M. H. J. Bollen, J. Lundquist. "Reliability study methodology for HVDC grids," presented at the Cigré Paris Session, paper B4-108, Paris, (2010).
[6] R. Svoma, M. Dickinson, C. Brown. “Subsea connections to high capacity offshore windfarms”, 19th International Conference on Electricity Distribution, Vienna, (2007).
[7] A. Sannino, H. Breder, E. Nielsen. “Reliability of Collection Grids for Large offshore Wind Parks”, 9th International Conference on Probabilistic Methods Applied to Power Systems, Stockholm, (2006).
[8] A. Underbrink, J. Hansen, A. Osterholt, W. Zimmerman. “Probabilistic Reliability Calculations for the Grid Connection of and Offshore Wind Farm”, 9th International Conference on Probabilistic Methods Applied to Power Systems, Stockholm, (2006).
[9] http://news.bbc.co.uk/1/hi/england/norfolk/7190082.stm accessed on 05/10/2016
[10] http://news.bbc.co.uk/1/hi/england/norfolk/7190082.stm accessed on 05/10/2016
[11] http://news.bbc.co.uk/1/hi/england/7290290.stm accessed on 05/10/2016
[12] http://www.windpoweroffshore.com/article/1191497/thanet-cable-failure-cost-vattenfall-%E2%82%AC5m Accessed on 06/10/2016
[13] http://www.windpoweroffshore.com/article/1323873/balfour-beatty-awarded-thanet-transmission-licence accessed on 05/10/2016
[14] http://www.4coffshore.com/windfarms/remedial-works-underway-for-thanet-nid4649.html accessed on 05/10/2016
[15] http://www.4coffshore.com/windfarms/pharos-recovers-faulty-walney-cable-nid3389.html accessed on 05/10/2016
[16] https://www.ofgem.gov.uk/sites/default/files/docs/tc_robin_rigg_-_direction_under_paragraph_10_of_amended_standard_condition_e12-j4.pdf accessed on 05/10/2016
[17] http://www.windpoweroffshore.com/article/1368848/horns-rev-2-cable-failure-confirmed-tso-updated accessed on 05/10/2016
[18] http://www.sunwindenergy.com/news/cable-damage-british-offshore-wind-farms accessed on 05/10/2016
[19] http://www.4coffshore.com/windfarms/anholt-cable-defects-nid1355.html accessed on 05/10/2016
[20] http://www.4coffshore.com/windfarms/walney-2-no-go-since-friday-nid2963.html accessed on 05/10/2016
[21] http://www.vbms.com/en/projects/detail/gwynt-y-mor-cable-repair accessed on 05/10/2016
[22] http://gymofto.co.uk/docs/Investor%20Report%20-%20March%202015.pdf accessed on 05/10/2016

## Slide 12
Questions ?
futurewind 2017 is sponsored by:
Organised by the Wind & Marine Energy Systems CDT